## VALORES
ITEM1 | 4000 | Real Energy, Consumption | kWh/Scale | E
ITEM2 | 4001
ITEM3 | 4002 | Apparent Energy, Consumption | kVAh/Scale | E
ITEM4 | 4003
ITEM5 | 4004 | Reactive Energy, Consumption | kVARh/Scale | E
ITEM6 | 4005
ITEM7 | 4006 | Real Power, Total | kW/Scale | W
ITEM8 | 4007 | Apparent Power, Total | kVA/Scale | W
ITEM9 | 4008 | Reactive Power, Total | kVAR/Scale | W
ITEM10 | 4009 | Power Factor, Total |  | 0.0001
ITEM11 | 4010 | Voltage, L-L, 3P Average | Volt/Scale | V
ITEM12 | 4011 | Voltage, L-N, 3P Average | Volt/Scale | V
ITEM13 | 4012 | Current, 3P Average | Amp/Scale | I
ITEM14 | 4013 | Frequency | Hz | 0.01
ITEM15 | 4014 | Real Power, Total Demand Present
ITEM16 | 4015 | Apparent Power, Total Demand Present
ITEM17 | 4016 | Reactive Power, Total Demand Present
ITEM18 | 4017 | Real Power, Total Demand Peak
ITEM19 | 4018 | Apparent Power, Total Demand Peak
ITEM20 | 4019 | Reactive Power, Total Demand Peak
ITEM21 | 4020 | Current, A | Amp/Scale | I
ITEM22 | 4021 | Current, B | Amp/Scale | I
ITEM23 | 4022 | Current, C | Amp/Scale | I
ITEM24 | 4023 | Current, N | Amp/Scale | I
ITEM25 | 4024 | Current, A, Demand Present
ITEM26 | 4025 | Current, B, Demand Present
ITEM27 | 4026 | Current, C, Demand Present
ITEM28 | 4027 | Current, A, Demand Peak
ITEM29 | 4028 | Current, B, Demand Peak
ITEM30 | 4029 | Current, C, Demand Peak
ITEM31 | 4030 | Voltage, A-B
ITEM32 | 4031 | Voltage, B-C
ITEM33 | 4032 | Voltage, C-A
ITEM34 | 4033 | Voltage, A-N
ITEM35 | 4034 | Voltage, B-N
ITEM36 | 4035 | Voltage, C-N
ITEM37 | 4036 | Real Power, A
ITEM38 | 4037 | Real Power, B
ITEM39 | 4038 | Real Power, C
ITEM40 | 4039 | Apparent Power, A
ITEM41 | 4040 | Apparent Power, B
ITEM42 | 4041 | Apparent Power, C
ITEM43 | 4042 | Reactive Power, A
ITEM44 | 4043 | Reactive Power, B
ITEM45 | 4044 | Reactive Power, C
ITEM46 | 4045 | Current, A, THD
ITEM47 | 4046 | Current, B, THD
ITEM48 | 4047 | Current, C, THD
ITEM49 | 4048 | Power Factor, Total Signed
ITEM50 | 4049 | Voltage, A-N, THD
ITEM51 | 4050 | Voltage, B-N, THD
ITEM52 | 4051 | Voltage, C-N, THD
ITEM53 | 4052 | Voltage, A-B, THD
ITEM54 | 4053 | Voltage, B-C, THD
ITEM55 | 4054 | Voltage, C-A, THD
ITEM56 | 4055 | Real Power, Total Minimum
ITEM57 | 4056 | Apparent Power, Total Minimum
ITEM58 | 4057 | Reactive Power, Total Minimun
ITEM59 | 4058 | Power Factor, Total Minimum
ITEM60 | 4059 | Frequency Minimum
ITEM61 | 4060 | Current, A, Minimum
ITEM62 | 4061 | Current, B, Minimum
ITEM63 | 4062 | Current, C, Minimum
ITEM64 | 4063 | Current, N, Minimum
ITEM65 | 4064 | Voltage, A-N,Minimum
ITEM66 | 4065 | Voltage, B-N,Minimum
ITEM67 | 4066 | Voltage, C-N,Minimum
ITEM68 | 4067 | Voltage, A-B,Minimum
ITEM69 | 4068 | Voltage, B-C,Minimum
ITEM70 | 4069 | Voltage, C-A,Minimum
ITEM71 | 4070 | Current, A, THD Minimum
ITEM72 | 4071 | Current, B, THD Minimum
ITEM73 | 4072 | Current, C, THD Minimum
ITEM74 | 4073
ITEM75 | 4074 | Voltage, A-N, THD Minimum
ITEM76 | 4075 | Voltage, B-N, THD Minimum
ITEM77 | 4076 | Voltage, C-N, THD Minimum
ITEM78 | 4077 | Voltage, A-B, THD Minimum
ITEM79 | 4078 | Voltage, B-C, THD Minimum
ITEM80 | 4079 | Voltage, C-A, THD Minimum
ITEM81 | 4080 | Real Power, Total Maximum
ITEM82 | 4081 | Apparent Power, Total Maximum
ITEM83 | 4082 | Reactive Power, Total Maximum
ITEM84 | 4083 | Power Factor, Total Maximum
ITEM85 | 4084 | Frequency Maximum
ITEM86 | 4085 | Current, A,Maximum
ITEM87 | 4086 | Current, B,Maximum
ITEM88 | 4087 | Current, C,Maximum
ITEM89 | 4088 | Current, N,Maximum
ITEM90 | 4089 | Voltage, A-N,Maximum
ITEM91 | 4090 | Voltage, B-N,Maximum
ITEM92 | 4091 | Voltage, C-N,Maximum
ITEM93 | 4092 | Voltage, A-B,Maximum
ITEM94 | 4093 | Voltage, B-C,Maximum
ITEM95 | 4094 | Voltage, C-A,Maximum
ITEM96 | 4095 | Current, A, THD Maximum
ITEM97 | 4096 | Current, B, THD Maximum
ITEM98 | 4097 | Current, C, THD Maximum
ITEM99 | 4098
ITEM100 | 4099 | Voltage, A-N, THD Maximum
ITEM101 | 4100 | Voltage, B-N, THD Maximum
ITEM102 | 4101 | Voltage, C-N, THD Maximum |  |  |  | -2
ITEM103 | 4102 | Voltage, A-B, THD Maximum |  |  | 10
ITEM104 | 4103 | Voltage, B-C, THD Maximum
ITEM105 | 4104 | Voltage, C-A, THD Maximum |  |  | 0.01
ITEM106 | 4105 | Scale Factor I (current)
ITEM107 | 4106 | Scale Factor V (voltage) |  |  | 100
ITEM108 | 4107 | Scale Factor W (power) |  |  | 10000
ITEM109 | 4108 | Scale Factor E (energy)
ITEM110 | 4109
ITEM111 | 4110 | Usage Hours
ITEM112 | 4111 | Usage Minutes
ITEM113 | 4112 | Error Bitmap

## formulas
| [4000] | 0 | 21000 | 8675 | 21E3
| [4001] | 0 | 3077 | 12002 | 2EE2
[5 empty] | 21E32EE2 | 568536802
|  |  |  | 65536 |  | 568536802
Si | ITEM2 == 0
EnergiaActivaConsumida_KWH | ( ( ITEM1 *65536 ) + ( ITEM2 ) ) * POWER( 10, ITEM109 )
si | ITEM2 < 0
EnergiaActivaConsumida_KWH | ( ( ITEM1 *65536 ) + ( ITEM2 +65536 ) ) * POWER( 10, ITEM109 )
si | ITEM2 > '0'
EnergiaActivaConsumida_KWH | ( ( ITEM1 *65536 ) + ( ITEM2 ) ) * POWER( 10, ITEM109 )
PotenciaActivaTotal_KW | ( ITEM7 ) * POWER( 10, ITEM108 )